**Section 215.60 Filling Densities**

a) Filling density is limited to 85% capacity by volume at 60°F.

b) The filling densities for non-refrigerated containers shall not exceed the following:

1) Uninsulated aboveground 56%;

2) Insulated aboveground 57%.

c) US Department of Transportation containers shall be filled in accordance with49 CFR 173.315(m)(5).

d) If containers are to be filled according to liquid level by any gauging method other than a fixed length dip tube gauge, each container shall have a thermometer well and thermometer so that the internal liquid temperature can be easily determined and the amount of liquid and vapor in the container corrected to a 60°F basis.

(Source: Amended at 40 Ill. Reg. 8704, effective July 1, 2016)